## DWF Exceedance
Year |  | 2016
Licence Number | Site Name | SEPA Measurement Point Description | Licence DWF (m3/d) | DWF (m3/d) | DWF > Licence (Y/N) | Number of consecutive years of exceeded | Exceedance Cause | Comments
CAR/L/12345678 | BIGTOWN WWTW | Bigtown WWTW influent flow | 5578 | 5660.3428 | Y | 1 | Suspected Increased infiltration | Marginal exceedance (1% over licence). There are known issues with influent flow meter, unclear whether this has an impact on DWF as issue currently believed to only affect higher flow rates. Radar rainfall indicates less rainfall in 2016 than 2015 so rainfall unlikely to be cause of exceedance. WICS annual return indicates no significant increase in population, trade or tourism.